## BOQ
SL. | MODEL NO | DESCRIPTION
PANELS
1 | AVANI | Supply, Installation and Commissioning, Installation and Commissioning of Addressable fire alarm Panel which consists of display board which will have 160 Character Display with Touch key pad, Mother board which will have ARM CORTEX M3 32 Bit Processor, Inbuilt RS-485 Networking Circuit for peer to peer networking, Inbuilt USB 2.0 Port for upload and download the Configuration tools, Two inbuilt programmable inputs, Two inbuilt NAC's, and Three Programmable Relays, and 4 Loop Card circuits. power Supply, Installation and Commissioning Board which will have SMPS fully protected board, which its operates on 120 to 220V AC ± 10% with 50/60 Hz, battery backup 24V DC with built-in charger. the panel have IP-50 rating Optional: for BMS integration thru MODBUS converter, Graphical Software, Software for TCP/IP Module, provision for GSM based Auto dialler, provision for printer thru compatible module, Approval: UL Listed, Make: Ravel
2 | Avani - LCS | Supply, Installation and Commissioning, Installation and Commissioning of Loop Card which will have 254 devices of both detectors and modules in a single line circuit on any combination, SLC should supports both Class A and Class B wiring. Shall have an LED indication for FIRE, Normal and Redundancy conditions Approval: UL Listed, Make: Ravel
3 | Avani (active repeater) | Supply, Installation and Commissioning, Installation and Commissioning of Addressable Active Repeater Panel which consists of display board which will have 160 Character Display with Touch key pad, Mother board which will have CORTEX 64 Bit Processor, Inbuilt RS-485 Networking Circuit for peer to peer networking, and One Fire Relays, power Supply, Installation and Commissioning Board which will have SMPS fully protected board, which operates on 120 to 220V AC ± 10% with 50/60 Hz, battery backup 24V DC with built-in charger. the panel have IP-50 rating - Approval: UL Listed, Make: Ravel
4 | Avani - PRP | Supply, Installation and Commissioning of Addressable Active Repeater Panel which consists of display board which will have 160 Character Display with Touch key pad, Mother board which will have CORTEX 64 Bit Processor, Inbuilt RS-485 Networking Circuit for peer to peer networking, and One Fire Relays, power Supply, Installation and Commissioning Board which will have SMPS fully protected board, which operates on 24V DC Input. The panel have IP-50 rating - Approval: UL Listed - Make: Ravel
DETECTORS
5 | RE - 317D SL | Supply, Installation and Commissioning of Addressable Smoke detector with base with Binary coded address setting. Dual LED’s for 360° visibility. Polarity Free, Sleek low-profile housing design. Regular 100mm base. IP Rating : IP - 42. Approval: UL Listed, Make: Ravel
6 | RE - 317D HL | Supply, Installation and Commissioning of Addressable Heat detector with Fixed temperature of 59°C and ROR feature to raise an alarm when the temperatures raises 11.1°per Minute, Shall have Binary coded address setting. Dual LED’s for 360° visibility. Non Polarised, Sleek low-profile housing design. Regular 100mm base. IP Rating : IP - 42. Approval: UL Listed, Make: Ravel
7 | RE - 317D SHL | Supply, Installation and Commissioning of Addressable Multi Sensor - Heat Cum Smoke detector with ROR features to raise an alarm when the temperature reaches 11.1°per Minute with base with Binary coded address setting. Dual LED’s for 360° visibility. Polarity free, Sleek low-profile housing design. Regular 100mm base. IP Rating : IP - 42. Approval: UL Listed, Make: Ravel
8 | RE - 314 BI | Supply, Installation and Commissioning of Fault isolator Base capable of monitoring shorted loop circuit and automatically restore communications when short circuit rectified, Shall have LED indication on the base to provide visual indication for any faults - Make: Ravel
9 | RE- 716 P | Supply, Installation and Commissioning of Manual Pull Station - Single Action/Dual action - with back box and Break Glass Rod, shall be resettable by Align key to avoid unauthenticated restorations - Approval: UL Listed - Make: Ravel NOTE: Need to connect with Monitor Module (RE - 717 MM)
10 | RE - 428 FR | Supply, Installation and Commissioning of Beam Detector comprising of 4 wire system with Infrared emitter and receiver in a single housing and single reflector plate - 5-50mtrs. Range - equipped with built-in automatic compensation - in-built laser light for easy alignment - Option for remote indication - Three sensitivity threshold of 18%, 30% & 50% - Make: Ravel
11 | RE - 428 HR | Supply, Installation and Commissioning of Beam Detector comprising of 4 wire system with Infrared emitter and receiver in a single housing and Four reflector plates - 5-100mtrs. Range - equipped with built-in automatic compensation - in-built laser light for easy alignment - Option for remote indication - Three sensitivity threshold of 18%, 30% & 50% - Make: Ravel
MODULES
12 | RE - 717 MC | Supply, Installation and Commissioning of Addressable Control Module for activating the Notification application devices. Shall have supervisory facility to supervise the auxiliary power Supply as well as the Notification Appliance Circuits.. Shall have Binary Coding Setting dip switches, Shall have an LED indication for normal working and active Modes - Approval: UL Listed, Make: Ravel
13 | RE - 717 MR | Supply, Installation and Commissioning of Addressable Relay Module with Non Supervised Dual potential free contacts. Shall have Binary Coded Dip Switch address settings, Shall have an LED indication for normal and active modes Approval: UL Listed, Make: Ravel
14 | RE - 717 MM | Supply, Installation and Commissioning of Addressable Monitor Module for monitoring the field NO/NC devices. Shall have Binary Coding Setting Dip Switch, Shall have an LED indication for normal and Active Modes - Approval: UL Listed, Make: Ravel
15 | RE - 717 MI | Supply, Installation and Commissioning of Fault isolator Base / Module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected - Make: Ravel
16 | RE - 717 MZ | Supply, Installation and Commissioning of Addressable Zone Interface Module for monitoring the field Conventional devices., Shall have Binary Coding address DIP switch Settings, Shall supports 16 conventional devices - Make: Ravel
ACCESSORIES
17 | RE - 24 CS | Supply, Installation and Commissioning of Conventional type Horn / Strobe wall mounted type rated at 100 ± 5 DBA @ 1m for Audible annunciation, Fire Sires Sound - ABS - Make: Ravel - Note: Need to Connect with Addressable Control Module
18 | RE - 24 SS | Supply, Installation and Commissioning of Conventional type Horn wall mounted type rated at 90 dBA @ 1m for Audible annunciation - Make: Ravel Note: Need to Connect with Addressable Control Module
19 | RE - RI | Supply, Installation and Commissioning of Response indicator for all detectors located above false ceiling and in closed cabins - Make: Ravel
20 | Avani - IP | Supply, Installation and Commissioning of TCP / IP Module (Ethernet Module) - to provide communication between local network that uses the RJ45 communication protocol (TCP server & UDP) and fire alarm control panels - Make: Ravel
21 | Avani Soft | Supply, Installation and Commissioning of Graphic Software - to monitor & control the status of the FACP from the windows based system - with Visual & Sound alerts for the fire and fault conditions - with Three Level multi users access - Make: Ravel
22 | Avani - CS | Supply, Installation and Commissioning of Configuration Software - GUI Based - Location Programming for each device - Monitor & Control the status of the FACP's from the PC - Make: Ravel
23 | RE - AMB | Supply, Installation and Commissioning of ModBus Converter to interface Fire Alarm Control Panel and RS 232 / RS 485 with Modbus protocol - Make: Ravel
24 | RE - 517 MMI | Supply, Installation and Commissioning of Annunciator Panel with 16 Windows with Point, Zone & System Status used with RS 485 interface - Make: Ravel
25 | RE - 517 MMI | Supply, Installation and Commissioning of Annunciator Panel with 32 Windows with Point, Zone & System Status used with RS 485 interface - Make: Ravel
26 | RE - 517 MMI | Supply, Installation and Commissioning of Annunciator Panel with 64 Windows with Point, Zone & System Status used with RS 485 interface - Make: Ravel
27 | RE-517 MG | Supply, Installation and Commissioning of GSM based message generator, shall have capability to send SMS to 10 nos., shall have message configuration facility, Shall show the exact location of the Devices as shown in the main fire alarm control panel, Shall be compatible with Main Control Panel. Make: Ravel