## AVANI
MONITI Device / Power Calculation
Secondary Power Source Requirements
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 5 Minutes | 0.084 | 24 Hours | 24
Device Type | Qty |  | Current Draw |  | Total | Qty |  | Current Draw |  | Total | 10 Minutes | 0.167 | 48 Hours | 48
Main Circuit Board | 1 | x | 0.12 | = | 0.12 | 1 | x | 0.17 | = | 0.17 | 15 Minutes | 0.25 | 60 Hours | 60
Loop Card | 0 | x | 0.04 | = |  | 0 | x | 0.085 | = |  | 20 Minutes | 0.334 | 72 Hours | 72
DC Output Power | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
4-wire Detector Heads | 0 | x | 0 | = |  | 0 | x | 0 | = |  | 30 Minutes | 0.5
Addressable Devices | [10 empty] | 45 Minutes | 0.75
RE-337-SH | 0 | x | 0.0005 | = | [6 empty] | 60 Minutes | 1
RE-337-S | 0 | x | 0.0005 | =
RE-337-H | 0 | x | 0.0005 | =
RE-737MC | 0 | x | 0.0005 | =
RE-737MM | 0 | x | 0.0005 | =
RE-737MR | 0 | x | 0.0005 | =
RE-737MZ | 0 | x | 0.0005 | =
RE-737MX | 0 | x | 0.0005 | =
RE-737M | 0 | x | 0.0005 | =
RE-24ES | 0 | x | 0.0005 | =
RE-374BS | 0 | x | 0.0005 | =
RE-716BI | 0 | x | 3e-05 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| 0 | x | 0 | =
| Maximum alarm draw for Addressable devices (SLC) | [8 empty] | 0
RE-24ES | 0 | x | 0 | = |  | 0 | x | 0.007 | =
RE-374BS | 0 | x | 0 | = |  | 0 | x | 0.007 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC | [5 empty] | 0 | x | 0 | =
Current Draw (non-alarm) |  |  | 0 | = |  |  |  | 0 | =
Sum each column for totals | Total Standby Current |  |  |  | 0.12 | Total Alarm Current |  |  |  | 0.17
MONITI Battery Calculation
Note: You can edit all current draws and are fully responsible for verifying these calculations. Only enter values in yellow cells.
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0.12 |  |  | x | 24 |  | = | 2.88
Required Alarm Time in Hours
20 Minutes
Alarm Load Current (Amps) |  |  | 0.17 |  |  | x | 0.334 |  | = | 0.05678
Standby and Alarm Load Subtotal | [8 empty] | = | 2.9368
Derating Factor | [8 empty] | = | 1.2
Total Ampere Hours Required | [8 empty] | = | 3.5241
Recommended Batteries: | [5 empty] | 7AH Batteries
Battery Check
The batteries can be charged by the AVANI Charger.
The batteries can be housed in the AVANI Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
The standby current is within the limitations of the panel.
The alarm current is within output limitations of the panel.
WIRING REQUIREMENT
CIRCUIT TYPE | WIRE TYPE AND LIMITATIONS |  |  |  | RECOMMENDED MAX. DISTANCE Feet (meters) |  |  | WIRE GUAGE
SLC | Untwisted, unshielded wire (Do not exceed 40 ohms) |  |  |  | 10,000 (3,000 m) 8,000 (2,400 m) 4,875 (1,480 m) 3,225 (975 m) |  |  | 12 AWG (3.25 mm2) Belden 9583 WPW999 14 AWG (2.00 mm2) Belden 9581 WPW995 16 AWG (1.30 mm2) Belden 9575 WPW991 18 AWG (0.75 mm2) Belden 9574 WPW975
Initiating Device Circuit | Untwisted, unshielded wire (Do not exceed 100 ohms) |  |  |  | 10,000 (3,000 m) 8,000 (2,400 m) 4,875 (1,480 m) 3,225 (975 m) |  |  | 12 AWG (3.25 mm2) Belden 9583 WPW999 14 AWG (2.00 mm2) Belden 9581 WPW995 16 AWG (1.30 mm2) Belden 9575 WPW991 18 AWG (0.75 mm2) Belden 9574 WPW975
24 VDC resettable, nonresettable | No more than 1.2 volt drop allowed from supply source to end of any branch |  |  |  | Distance limitation set by 1.2 volt maximum line drop |  |  | 12 AWG (3.25 mm2) - 18 AWG (0.75 mm2)
Note on B38: Current limitation of Terminal TB4 circuits is 3.0 Amps per NAC.
Note on E10: Refer to the Device Compatibility Document for standby current.
Note on E49: Value from Total Standby Load cell.
Note on E52: Value from Alarm Standby Load cell.
Note on H48: Select Standby Time in Hours from the dropdown list.
Note on H51: Select the Alarm Time in minutes from the dropdown list.
Note on L54: Select the Derating Factor from the dropdown list.