## Sheet1
RAVEL ELECTRONCIS PVT LTD
Battery Calculation
Entries only to be made in the Yellow cell locations
|  | Number of |  | Current |  | Total Current
Device Type |  | Zone / Hooters |  | (Amps) |  | (Amps)
Quiescent Current | [5 empty] | 0.05
IDC Standby Current |  |  | X | 0.0068 | = | 0
Total Current in Normal Condition |  | 0.05
Alarm Current |  | 1 | X | 0.06 | = | 0.06
No. of Sounder (RE-MHR) |  |  | X | 0.2 | = | 0
No. Strobe Cum Sounder (RE-24SS) |  |  | X | 0.1 | = | 0
No. Sounder (RE-24CS) |  |  | X | 0.05 | = | 0
Total Current in Alarm Condition |  | 0.06
Hours
Normal Condition |  | 48 | X | 0.05 | = | 2.4
Alarm Condtion |  | 0.0833 | X | 0.06 | = | 0.004998
SUM COLUMN FOR STANDBY LOAD |  |  |  | 2.886 | = | AMPS
Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.
Note on D12: Ramesh: No. Of Zones?
Note on D16: Ramesh: No. Of Zones?