## Sheet1
RAVEL ELECTRONCIS PVT LTD
Battery Calculation (EK-740)
Entries only to be made in the Yellow cell locations | [7 empty] | 1 | 5 Minutes | 0.084 | 24 Hours | 24
[7 empty] | 8 | 2 | 10 Minutes | 0.167 | 48 Hours | 48
|  | Number of |  | Current |  | Total Current |  | 3 | 15 Minutes | 0.25 | 60 Hours | 60
Device Type |  | Zone / Hooters |  | (Amps) |  | (Amps) |  | 4 | 20 Minutes | 0.334 | 72 Hours | 72
[8 empty] | 5 | 25 Minutes | 0.417 | 90 Hours | 90
Quiescent Current | [5 empty] | 0.113 |  | 6 | 30 Minutes | 0.5
[8 empty] | 7 | 45 Minutes | 0.75
IDC Standby Current |  | 8 | X | 0.0068 | = | 0.0544 |  | 8 | 60 Minutes | 1
Total Current in Normal Condition |  | 0.1674
Alarm / Zone ON Current |  | 2 | X | 0.036 | = | 0.072
Total Current in Alarm Condition | [5 empty] | 0.072
Hours
Normal Condition |  | 24 Hours
|  | 24 | X | 0.1674 | = | 4.0176
Alarm / Zone ON Condtion |  | 5 Minutes
|  | 0.084 | X | 0.072 | = | 0.006048
SUM COLUMN FOR STANDBY LOAD |  |  |  | 4.8284 | = | AMPS
Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.
Note on D12: Ramesh: No. Of Zones?
Note on D16: Ramesh: No. Of Zones?